Flame Detection

Engineering Specifications

## October, 2012

Safe Fire Detection Inc.

5915 Stockbridge Dr.

Monroe, NC 28110

Phone: (704) 821-7920

Fax:     (704) 821-4327

Website: www.safefiredetection.com

E-mail: staff@safefiredetection.com

Pub. #MA-SFES1012

SAFEFLAME FLAME DETECTOR

ENGINEERING SPECIFICATIONS

CSI SECTION  [             ]

FLAME DETECTION SYSTEM (S)

PART 1 - GENERAL

1.01	SUMMARY

A.  Section includes linear heat detection systems

B.  Related Sections:

- Section 16720 - Fire Alarm and Detection Systems

- Section 15300 - Fire Protection Systems

1.02	REFERENCES

A.  National Fire Protection Association (NFPA):

- NFPA 72 Standard for Protection Signaling Systems

- Factory Mutual Insurance (FM) Approval Guide

- ATEX Product Certification for use in potentially explosive enviornments

B. State and Local Codes.

1.03	SYSTEM DESCRIPTION

- Design Requirements:

  - Shall consist of an approved flame detector and control/releasing panel that are designed and installed to detect the flame from a fire as it was designed.

  - The control/releasing panel shall be any approved self-contained, micro-controlled base technology that indicates alarms, faults and system integrity or as approved by the manufacturer. The intent of the panel is to alarm when the flame detector senses a fire and either alarm, or alarm and release an extinguishing agent. The panel shall also have 24, 60 or 90 (Choose One) hour battery back up.

  - The flame detection systems spacing shall be determined by NFPA, State Codes, Local Codes and the manufacturer’s recommendations.

B.  Performance Requirements:

- Shall be FM tested and approved.

- Shall be listed for up to 200 foot spacing (IR3) or 100 foot spacing (UV/IR).

- Shall be compatible with any UL listed fire alarm panel.

- Must not require proprietary panel.

- Shall report any equipment related fault through a fault output relays.

- Shall be installed to comply with NFPA standards (and the authority having jurisdiction).

1.04	SUBMITTALS

- Submit product data and shop drawings including isometric and plan view layouts of the system under provisions of section [                 ].

- Supply one copy of the manufacturers Installation & Operation Manuals after completion of installation.

- Supply one copy of the manufacturers Start-Up forms within 30 days after installed and commissioned.

- Each bidder must supply their proposed system design for the area(s) to be protected together with a letter certifying that the design strictly complies with the limitations established by the manufacturer.

1.05	QUALITY ASSURANCE

A.  Qualifications:

- Contractor:  The contractor shall have a minimum of 5 years experience in the design and installation of fire detection systems.

- Equipment suppliers:  The equipment suppliers shall be factory authorized 	   and trained by the manufacturer every other year to design, install and maintain all aspects of the system.

B.  Regulatory Requirements:

- Codes and approvals:  Equipment supplier shall conform to the local code requirements and approvals applicable to this section.  Supplier must obtain and pay all necessary permits prior to beginning work in this section.

- The system shall be Factory Mutual approved.

1.06	PROJECT CONDITIONS

A.  Physical/Environmental Requirements:  (CHOOSE APPROPRIATE)

- The detector shall be permanently mounted where specified on the shop drawings or in a location to facilitate access and ease of service.

- The detector must be mounted in an ambient temperature range of -40° to +167° Fahrenheit.

- Where the environment is harsh, the releasing control panel shall be fitted with a NEMA 4 or NEMA 12 (Choose One) enclosure.

- The detector shall be installed in compliance with [            ] ATEX standards for potentially explosive enviornments.

1.07	SEQUENCING and SCHEDULING

- Coordinate work performed under this section with work specified in other sections as noted in Section [              ].

1.08	MAINTENANCE

- Maintenance Service:  Shall be provided by a factory authorized and factory trained representative in accordance with the manufacturers, NFPA 72 and local requirements of the authority having jurisdiction.

PART 2 - PRODUCTS

2.01	MANUFACTURER

- Flame Detection System:

Acceptable Manufacturer:   Safe Fire Detection, Inc.

5915 Stockbridge Dr.

Monroe, NC  28110

Ph.: 704-821-7920    Fax: 704-821-4327

- Detection Method: Flame Detection: (CHOOSE ONE) UV/IR or IR3

2.02	MANUFACTURED PRODUCTS

A.  The Flame Detector (choose one):

UV/IR Aluminum (Standard)	Model #: SF100A

UV/IR Stainless Steel (Explosion Proof)	Model #: SF100SX

IR3 Aluminum (Standard)	Model #: SF200A

IR3 Stainless Steel (Explosion Proof)	Model #: SF200SX

2.03	COMPONENTS

A.  The Flame Detection System:

- UL listed Addressable Panel or Conventional panel.

- The detection principle shall be UV/IR or IR3 type, and be capable of detecting fires as it was designed.

2.04	EQUIPMENT

- The control panel for the flame detection releasing system must be a microprocessor-based control capable of protecting multiple hazards in one control panel. It shall be U/L listed under Standard 864 for Local Control Units for Releasing Service. The control must also be approved by FM and be compatible with the requirements of NFPA -72 (Local: A, M, SS service types; NC signaling type) and NFPA –13, NFPA –15, and NFPA –16.

- The flame detector shall be a multi-spectral range detector consisting of either a UV and IR sensor or three IR sensors capable of detecting the radiation given off by a flame in the ultraviolet and/or infrared spectral ranges.

### PART 3 - EXECUTION

3.01	INSTALLATION

A.  The Flame Detection System: The contractor shall install the system in accordance with the manufacturer's installation recommendations and Operational Manual.

3.02	FIELD QUALITY CONTROL

A.  Tests and Commissioning:

- The contractor shall commission the complete installation in the presence of the end user or their appointed representative.

- The contractor shall provide materials all necessary instrumentation, test equipment, labor.

- The contractor shall record all test and commissioning requirements and a copy shall be provided to the end user or an authorized representative.

- Checks must be made to ensure that all ancillary equipment and warning devices are operational as designed and specified with care taken not to discharge a suppression system.

- The contractor shall upon completion of commissioning and testing provide the end user or authorized representative with the isometric as-built drawings as well as the System Start-Up forms, Installation and Operation manuals.

- The contractor shall be or be represented by an authorized representative of SAFE Fire Detection, Inc. This person must have successfully completed SAFE’s technical training seminar and show proof of it by means of a valid certificate. The company listed on the certificate at the time of the testing and commissioning must employ, this person who must be present or the certificate is not valid.  The certificate is valid for a period of two years from the date on the certificate.